## Emergency Engine Log-Final
Emergency Engine Operating Log
Property : |  | K-12 School/Daycare Within 500' |  | Yes or No | Equipment # (PTO No.):
Air District Regulations: Permit must be posted within 25' of engine. The permit limits testing and maintenance hours- include the specific permitted hours below:
Maximum Annual Maintenance and Testing Hours: |  |  |  |  | Maximum Annual Total Operation Hours (if applicable):
Maximum Monthly Maintenance and Testing Hours (if applicable):
Required Run-Time: Emergency engine must be tested bi-weekly for 30 mins for diesel generators and weekly for diesel fire pumps (unless stricter permitted hour limits do not allow). Complete testing prior to 7:30 am in all cases. An engine located within 500' of a K-12 school cannot operate for non-emergency use between 7:30 a.m. and 3:30 p.m. on days when school is in session, although engines with diesel particulate filters are exempt from this restriction. Note that 500' is measured from exhaust stack outlet to school/daycare outer property line boundary.
NFPA 110: Requires all Transfer Switches to be tested and Generators to operate under load monthly for 30 mins.
# | OPERATIONAL ITEM | RANGE | LOG INFORMATION
Required by Air Permit (Applys to Generator & Fire Pump)
1 | Record Date of Test / Operation | Month / Day / Year
2 | Record Engine Run Start Time (circle am/pm) | Start Times | am / pm | am / pm | am / pm | am / pm
3 | Record Engine Stop Time (circle am/pm) | End Times | am / pm | am / pm | am / pm | am / pm
4 | Reason For Operation | Test, Emergency, Other
5 | Record Prestart Run-Time Reading | From Non-resettable meter (##.#)
6 | Record Post Run-Time Reading | From Non-resettable meter (##.#)
7 | Subtract Difference Between Post and Pre Run-Time Reading | Run Time Difference
8 | Test Performed By (Test, Maint., Power loss) | Signature
Generator Maintenance Checklist
9 | Check Crankcase Engine Oil Level | As indicated on dipstick
10 | Verify Fuel Level - Main Tank | Min - 2/3rds
11 | Verify Fuel Level - Day Tank (If Applicable) | Min - 2/3rds
12 | Verify Fuel Pump Operation (If Applicable) | Operational - √
13 | Check Cooling System (Radiator) Water Level | Full - √
14 | Verify Water Jacket Heater Operation | Operational - √
15 | Inspect Hoses and Belts for cracking and wear | Good/Fair/Poor
16 | Inspect Electrical Control Panel | Burn Marks/Loose wires
17 | Inspect Battery Terminals | No Corrosion
18 | Check Battery Electrolyte Level | Full - √
19 | Check Battery Specific Gravity - Monthly | 1.250 - 1.750
20 | Record Battery Voltage (12VDC) or (24VDC) | 13.3-13.6 / 26.6-27.2
21 | Check Battery Indicator Lamps | On - √
22 | Check Alarm Pilot Indicator Lamps | Off - √ (Test)
23 | Transfer Switch Test - Monthly (NFPA 110) Run under load for 30 mins | Auto-Start by tripping ATS breaker
24 | Transfer Time after Power Loss | 0-10 seconds
25 | Estimated Cranking Time in Seconds | 0-10 seconds
26 | Estimated Seconds to Reach Running Speed | 0-10 seconds
27 | Record Hertz | 60
28 | Record Voltage - Phase 1/2/3 | 480/480/480
29 | Record Amperage-Phase 1/2/3 | 00/00/00
30 | Water Temperature Reading | 170°F - 190°F
31 | Record Oil Pressure Reading | 40-70 PSI
32 | Record Fuel Pressure Reading | Not below 30 PSI
33 | Record Motor RPM's | RPM
34 | Verify Adequate Air-Flow Through Radiator | No blockage in fins
35 | Check for Unusual Noises, Heat, and Vibrations | None
36 | Check Excessive Exhaust Smoke | Not "Thick Black"
37 | Check Exhaust System for Leaks or Damage | Good/Fair/Poor
38 | Drain Exhaust Condensate Trap (if applicable) | Yes/No
39 | Inspect for Leaks of Any Kind | No Water, Oil, or Fuel Leaks
40 | Diesel Particulate Filter Back-Pressure (if applicable) | PSI
41 | Transfer Time after Power Restore | 0-10 mins
42 | General Shutdown Check | No Problems - OK
43 | Reset Controls to Automatic Position | "Auto"